071606T4MCT

MECHATRONIC TECHNICIAN LEVEL 6

ENG/OS/MC/CR/07/6

Manage Mechatronic Projects

TAITA TAVETA NATIONAL POLYTECHNIC

RESEARCH PROPOSAL

PROPOSED TITLE OF THE PROJECT :     SMART TRANSFORMER HEALTH MONITORING SYSTEM

NAME:                                                         STEPHEN NGIGE NGUGI

ADM NUMBER	:                                        20331

SUPERVISOR’S NAME:                              COLLINS MUTAI

CHAPTER ONE	1

1.0 INTRODUCTION	1

1.1 Background and Context	1

1.2 Problem Statement	2

1.3 Research Rationale	2

1.4 Research Aim	3

1.5 Research Objectives	3

General Objective	3

Specific Objectives	3

1.6 Research Questions	4

CHAPTER TWO	5

2.0 LITERATURE REVIEW	5

2.1 Key Concepts, Theories and Previous Studies	5

2.1.1 Power Transformers	5

2.1.2 Transformer Health Monitoring	5

2.1.3 Internet of Things (IoT)	6

2.1.4 Predictive Maintenance	6

2.1.5 ESP32 Microcontroller	7

2.1.6 Sensors Used in the Proposed System	8

2.2 Previous Studies	8

2.3 Key Debates and Controversies	9

2.4 Research Gap	10

CHAPTER THREE	11

3.0 METHODOLOGY	11

3.1 Research Design	11

3.2 System Design	11

System Inputs	12

System Outputs	12

3.3 Hardware Requirements	13

3.4 Software Requirements	13

3.5 Data Collection	14

3.6 Sampling	14

3.7 Data Analysis	15

3.8 System Operation	15

3.9 System Testing and Validation	16

3.10 Practical Considerations	17

CHAPTER FOUR	18

4.0 PRACTICALITIES	18

4.1 Implications and Contributions to Knowledge	18

4.1.1 Practical Implications	18

4.1.2 Theoretical Implications	19

4.2 Project Plan and Timeline	19

Gantt Chart	20

4.3 Budget	20

CHAPTER FIVE	22

References	22

APPENDICES	23

Appendix A: System Block Diagram	23

Appendix C : Bill of Materials (BOM)	24

CHAPTER ONE

1.0 INTRODUCTION

1.1 Background and Context

Electrical power transformers are among the most critical components in power generation, transmission, and distribution systems. They are responsible for transferring electrical energy between circuits while maintaining the required voltage levels. Transformers are widely used in power substations, industries, hospitals, educational institutions, manufacturing plants, and commercial buildings. Their reliable operation is essential for maintaining a continuous and stable supply of electricity.

In many developing countries, including Kenya, transformer inspection is largely carried out through routine manual maintenance. This method is time-consuming, labour-intensive, and often fails to identify faults before they become critical. As a result, many transformers fail unexpectedly, leading to interruptions in electricity supply and increased maintenance costs.

This project proposes the design and implementation of a Smart Transformer Health Monitoring System using an ESP32 microcontroller and IoT technology. The system will continuously monitor important transformer parameters such as temperature, load current, input voltage, oil level, and vibration. The collected data will be displayed locally on an LCD and transmitted remotely through a wireless communication platform. Whenever any monitored parameter exceeds the safe operating limit, the system will generate an alarm and notify the maintenance personnel, allowing corrective action to be taken before transformer failure occurs.

The proposed system will contribute to improving transformer reliability, reducing maintenance costs, minimizing downtime, and enhancing the overall efficiency of power distribution systems.

1.2 Problem Statement

Power transformers play a vital role in ensuring reliable electricity distribution. However, many transformers experience unexpected failures due to overheating, overloading, excessive vibration, low oil levels, and voltage abnormalities. In most cases, these faults are only discovered during routine inspections or after the transformer has already failed.

Manual inspection methods are inefficient because they do not provide continuous monitoring or early fault detection. Consequently, utilities and industries experience unplanned outages, high repair costs, reduced equipment lifespan, and disruption of essential services.

There is therefore a need for an intelligent monitoring system capable of continuously tracking the operating condition of transformers, detecting abnormal conditions in real time, and notifying maintenance personnel immediately. Such a system would significantly reduce transformer failures, improve maintenance planning, and increase the reliability of electrical power systems.

1.3 Research Rationale

The increasing demand for reliable electricity requires modern maintenance approaches that prevent equipment failure before it occurs. Traditional maintenance methods are mainly reactive, meaning that maintenance is performed after faults have already developed. This approach increases operational costs and reduces system reliability.

The proposed Smart Transformer Health Monitoring System introduces predictive maintenance by continuously monitoring transformer operating conditions using multiple sensors and IoT technology. The system will provide maintenance personnel with real-time information, enabling timely decision-making and reducing unnecessary maintenance activities.

The findings of this research will benefit:

- Kenya Power and other electricity distribution companies by reducing transformer failures.

- Manufacturing industries through improved reliability of industrial transformers.

- Hospitals and institutions by minimizing unexpected power interruptions.

- Maintenance engineers by simplifying transformer inspection.

- Students and researchers by providing a practical application of IoT in electrical maintenance.

- The mechatronics field by demonstrating the integration of sensors, embedded systems, and wireless communication in predictive maintenance.

1.4 Research Aim

To design and develop a Smart Transformer Health Monitoring System using ESP32 and IoT technology for continuous monitoring of transformer operating conditions and early fault detection.

1.5 Research Objectives

General Objective

To develop an intelligent transformer monitoring system capable of detecting abnormal operating conditions and providing real-time alerts.

Specific Objectives

- To design a transformer monitoring system using the ESP32 microcontroller.

- To monitor transformer temperature continuously.

- To measure transformer load current and voltage in real time.

- To detect excessive transformer vibration.

- To monitor transformer oil level.

- To transmit transformer operating data through an IoT platform.

- To generate visual and audible alarms whenever abnormal operating conditions are detected.

- To evaluate the performance and reliability of the developed monitoring system.

1.6 Research Questions

The study seeks to answer the following questions:

- How can IoT technology improve transformer health monitoring?

- Which transformer parameters are most important for early fault detection?

- How effective is the ESP32 in monitoring multiple transformer parameters simultaneously?

- Can the proposed system provide reliable real-time alerts before transformer failure occurs?

- How can continuous transformer monitoring reduce maintenance costs and equipment downtime?

CHAPTER TWO

2.0 LITERATURE REVIEW

2.1 Key Concepts, Theories and Previous Studies

2.1.1 Power Transformers

A power transformer is a static electrical device that transfers electrical energy from one circuit to another through electromagnetic induction. It is used to step up or step down voltage levels while maintaining the same frequency. Transformers are essential in power generation, transmission, and distribution because they enable efficient delivery of electricity over long distances.

The health of a transformer depends on several operating parameters such as temperature, load current, voltage, oil level, and mechanical vibration. Continuous monitoring of these parameters helps identify faults before they develop into major failures.

2.1.2 Transformer Health Monitoring

Transformer health monitoring is the continuous assessment of a transformer's operating condition using sensors and intelligent monitoring devices. The objective is to detect abnormal conditions at an early stage and provide maintenance personnel with sufficient time to take corrective action.

Traditional transformer maintenance relies on periodic inspections, which may fail to detect faults that develop between inspection intervals. Modern monitoring systems overcome this limitation by providing continuous real-time monitoring.

Common parameters monitored include:

- Transformer winding temperature

- Load current

- Input and output voltage

- Oil level

- Oil temperature

- Vibration

- Humidity (for some transformer designs)

2.1.3 Internet of Things (IoT)

The Internet of Things (IoT) refers to a network of physical devices connected to the internet that collect, process, and exchange data automatically.

In industrial maintenance, IoT enables engineers to monitor equipment remotely without being physically present. Sensor data can be transmitted through wireless communication to cloud platforms, allowing operators to access real-time information using smartphones or computers.

In this project, the ESP32 microcontroller serves as the IoT gateway by collecting sensor data and transmitting it via Wi-Fi.

2.1.4 Predictive Maintenance

Predictive maintenance is a maintenance strategy that uses real-time equipment data to predict faults before failure occurs.

Unlike corrective maintenance, which repairs equipment after failure, or preventive maintenance, which follows fixed maintenance schedules, predictive maintenance continuously evaluates equipment condition and recommends maintenance only when necessary.

Benefits include:

- Reduced maintenance costs

- Improved equipment lifespan

- Reduced downtime

- Increased operational reliability

- Enhanced worker safety

The proposed transformer monitoring system adopts this maintenance approach by continuously monitoring transformer health.

2.1.5 ESP32 Microcontroller

The ESP32 is a low-cost, high-performance microcontroller developed for embedded and IoT applications. It includes built-in Wi-Fi and Bluetooth communication, making it suitable for remote monitoring projects.

Advantages of using ESP32 include:

- Integrated Wi-Fi

- High processing speed

- Multiple analog and digital input/output pins

- Low power consumption

- Compatibility with Arduino IDE

- Support for cloud-based monitoring platforms

These features make the ESP32 suitable for monitoring several transformer parameters simultaneously.

2.1.6 Sensors Used in the Proposed System

The proposed system uses multiple sensors to monitor transformer operating conditions.

Temperature Sensor

The temperature sensor measures transformer temperature. Excessive temperature indicates overload, cooling system failure, or insulation deterioration.

Current Sensor (ACS712)

The ACS712 sensor measures transformer load current. High current may indicate overload or short-circuit conditions.

Voltage Sensor (ZMPT101B)

This sensor measures AC voltage supplied to the transformer. Voltage abnormalities may affect transformer performance and lifespan.

Oil Level Sensor

A float-type oil level sensor monitors transformer insulating oil. Low oil level may result from leakage and reduces insulation and cooling efficiency.

Vibration Sensor

Mechanical vibration is an indicator of internal faults, loose connections, or mechanical stress within the transformer.

2.2 Previous Studies

Several researchers have developed transformer monitoring systems using different sensing and communication technologies.

Many earlier systems monitored only one parameter, such as temperature or load current. While these systems improved fault detection, they could not provide a complete assessment of transformer health.

Other researchers introduced GSM-based monitoring systems that transmit fault notifications using SMS. Although effective for remote notification, these systems provide limited data visualization and storage.

Recent studies have adopted IoT technologies that allow transformer data to be displayed on cloud platforms. These systems improve accessibility and enable engineers to monitor transformers from any location with internet connectivity.

However, many existing systems remain expensive due to the use of industrial-grade equipment or focus on only a limited number of transformer parameters.

2.3 Key Debates and Controversies

One major debate in transformer maintenance concerns whether utilities should continue using traditional periodic maintenance or adopt predictive maintenance technologies.

Supporters of traditional maintenance argue that routine inspections are less expensive and require minimal technological investment.

However, many researchers argue that predictive maintenance provides greater long-term benefits because it reduces unexpected failures, maintenance costs, and equipment downtime.

Another debate concerns communication technologies. Some systems rely on GSM communication, while others use Wi-Fi-based IoT platforms. GSM offers wider coverage but incurs operational costs for SIM cards and SMS services. Wi-Fi-based IoT systems are more economical in areas with reliable internet access and provide richer data visualization.

2.4 Research Gap

Although many transformer monitoring systems have been developed, several limitations remain.

Most existing systems monitor only one or two transformer parameters, making it difficult to accurately assess overall transformer health. Others rely on expensive industrial monitoring equipment, limiting their adoption in small industries and educational institutions.

Furthermore, many systems lack real-time data visualization, remote monitoring capabilities, and integrated fault alert mechanisms.

This project addresses these gaps by developing a low-cost Smart Transformer Health Monitoring System using an ESP32 microcontroller. The system integrates temperature, current, voltage, oil level, and vibration sensors into a single platform, enabling continuous real-time monitoring and remote fault notification through IoT. The proposed design is affordable, scalable, and suitable for practical implementation in industries, educational institutions, and power distribution networks.

CHAPTER THREE

3.0 METHODOLOGY

3.1 Research Design

This study will adopt an experimental research design involving the design, development, testing, and evaluation of a Smart Transformer Health Monitoring System. The project will integrate sensors, an ESP32 microcontroller, and IoT technology to continuously monitor transformer operating conditions.

The experimental design is appropriate because it allows the researcher to build a prototype, collect real-time data, evaluate its performance, and determine whether the proposed system can accurately detect transformer faults.

The project will follow these stages:

- Requirement analysis

- System design

- Hardware development

- Software development

- Prototype construction

- System testing

- Performance evaluation

- Documentation

3.2 System Design

The proposed system consists of five sensing units connected to an ESP32 microcontroller.

The sensors continuously collect information about the transformer's operating condition. The ESP32 processes the sensor data, displays it on an LCD screen, and uploads it to an IoT platform via Wi-Fi. Whenever any parameter exceeds the preset safety limit, the system activates a buzzer and sends an alert to the maintenance personnel.

System Inputs

- Transformer temperature

- Transformer current

- Transformer voltage

- Oil level

- Mechanical vibration

System Outputs

- LCD display

- IoT dashboard

- Buzzer alarm

- Fault notification

- Relay (optional automatic shutdown)

3.3 Hardware Requirements

The proposed hardware includes:

| Component | Purpose |
| --- | --- |
| ESP32 Development Board | Main controller |
| DS18B20 Temperature Sensor | Measures transformer temperature |
| ACS712 Current Sensor | Measures transformer load current |
| ZMPT101B Voltage Sensor | Measures AC voltage |
| Float Switch | Monitors transformer oil level |
| SW-420 Vibration Sensor | Detects abnormal vibration |
| 20×4 I2C LCD | Displays measured values |
| Buzzer | Audible warning |
| Relay Module | Disconnects transformer during severe faults (optional) |
| Wi-Fi Module | Built into ESP32 |
| Power Supply | Powers the system |

3.4 Software Requirements

The following software tools will be used:

- Arduino IDE

- ESP32 Board Package

- Proteus Professional (simulation)

- Blynk IoT Platform (or ThingSpeak)

- GitHub (source code backup)

- Microsoft Word (documentation)

3.5 Data Collection

The system will collect data directly from sensors installed on the transformer prototype.

The collected parameters include:

- Temperature (°C)

- Current (A)

- Voltage (V)

- Oil level (High/Low)

- Vibration level

Sensor readings will be recorded at regular intervals and displayed locally on the LCD while simultaneously being transmitted to the IoT dashboard.

3.6 Sampling

The study will use purposive sampling, where one transformer prototype is selected for testing because it contains all the necessary operating conditions required to evaluate the proposed monitoring system.

Different fault conditions will be simulated, including:

- High temperature

- Overload current

- Low voltage

- Oil leakage

- Excessive vibration

These tests will determine the system's ability to detect abnormal conditions accurately.

3.7 Data Analysis

The collected sensor data will be analyzed using descriptive statistical methods.

The analysis will involve:

- Comparing measured values with predefined safety limits.

- Determining system response time.

- Evaluating sensor accuracy.

- Assessing alarm reliability.

- Evaluating communication reliability between the ESP32 and IoT platform.

Graphs showing changes in temperature, voltage, and current over time will be generated to assess system performance.

3.8 System Operation

The developed system will operate as follows:

- The ESP32 powers up and initializes all sensors.

- The temperature sensor measures transformer temperature.

- The current sensor measures load current.

- The voltage sensor measures input voltage.

- The oil level sensor checks transformer oil level.

- The vibration sensor detects abnormal mechanical movement.

- The ESP32 processes all sensor readings.

- Results are displayed on the LCD.

- The same data are uploaded to the IoT platform through Wi-Fi.

- If any parameter exceeds the preset limit:

- The buzzer is activated.

- A fault notification is sent to the user.

- The relay disconnects the load (optional).

3.9 System Testing and Validation

The developed prototype will be tested under different operating conditions to determine its effectiveness.

The following tests will be performed:

Temperature Test

The transformer temperature will be increased gradually to determine whether the system generates an alarm at the preset limit.

Current Test

Different electrical loads will be connected to verify whether overload conditions are correctly detected.

Voltage Test

The input voltage will be varied to observe the system's response to under-voltage and over-voltage conditions.

Oil Level Test

The oil level sensor will be manually adjusted to simulate oil leakage and verify the alarm operation.

Vibration Test

Mechanical vibration will be introduced to determine whether the vibration sensor detects abnormal movement.

3.10 Practical Considerations

Several challenges may be encountered during the implementation of the project.

These include:

- Limited availability of transformer testing equipment.

- Sensor calibration requirements.

- Wi-Fi connectivity interruptions.

- Power supply stability.

- Budget constraints.

- Time limitations.

These challenges will be minimized by using reliable components, careful calibration, and repeated testing throughout the development process.

CHAPTER FOUR

4.0 PRACTICALITIES

4.1 Implications and Contributions to Knowledge

The proposed Smart Transformer Health Monitoring System contributes to the growing adoption of intelligent maintenance systems in the electrical power sector. By integrating sensors, the ESP32 microcontroller, and IoT technology, the project demonstrates how real-time monitoring can improve transformer reliability and reduce operational costs.

The project also serves as an educational model for students and researchers interested in embedded systems, industrial automation, and predictive maintenance.

4.1.1 Practical Implications

The developed system is expected to provide the following practical benefits:

- Continuous monitoring of transformer operating conditions.

- Early detection of faults before transformer failure occurs.

- Reduction in maintenance costs through predictive maintenance.

- Improved reliability of electricity distribution.

- Reduced downtime caused by unexpected transformer failures.

- Enhanced safety for maintenance personnel.

- Remote monitoring of transformers through an IoT platform.

- Affordable monitoring solution suitable for industries, institutions, and utility companies.

4.1.2 Theoretical Implications

This project contributes to knowledge in several areas of mechatronics and electrical engineering by:

- Demonstrating the integration of embedded systems with IoT.

- Supporting predictive maintenance techniques for electrical equipment.

- Providing a practical application of sensor fusion.

- Expanding knowledge on smart condition monitoring systems.

- Offering a foundation for future research in intelligent transformer diagnostics.

4.2 Project Plan and Timeline

The project is expected to be completed within 16 weeks.

| Activity | Weeks |
| --- | --- |
| Proposal writing and approval | 1–2 |
| Literature review | 3–4 |
| System design | 5–6 |
| Procurement of components | 7 |
| Circuit design and simulation | 8–9 |
| Hardware assembly | 10–11 |
| Programming of ESP32 | 12 |
| System integration | 13 |
| Testing and troubleshooting | 14 |
| Documentation | 15 |
| Final presentation and submission | 16 |

Gantt Chart

| Activity | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Proposal | █ | █ |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Literature Review |  |  | █ | █ |  |  |  |  |  |  |  |  |  |  |  |  |
| System Design |  |  |  |  | █ | █ |  |  |  |  |  |  |  |  |  |  |
| Component Purchase |  |  |  |  |  |  | █ |  |  |  |  |  |  |  |  |  |
| Simulation |  |  |  |  |  |  |  | █ | █ |  |  |  |  |  |  |  |
| Hardware Construction |  |  |  |  |  |  |  |  |  | █ | █ |  |  |  |  |  |
| Programming |  |  |  |  |  |  |  |  |  |  |  |  | █ |  |  |  |
| Integration |  |  |  |  |  |  |  |  |  |  |  |  |  | █ |  |  |
| Testing |  |  |  |  |  |  |  |  |  |  |  |  |  |  | █ |  |
| Documentation |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | █ |
| Presentation |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

4.3 Budget

| Item | Quantity | Unit Cost (KSh) | Total (KSh) |
| --- | --- | --- | --- |
| ESP32 Development Board | 1 | 1,500 | 1,500 |
| ACS712 Current Sensor | 1 | 450 | 450 |
| ZMPT101B Voltage Sensor | 1 | 500 | 500 |
| DS18B20 Temperature Sensor | 1 | 350 | 350 |
| SW-420 Vibration Sensor | 1 | 250 | 250 |
| Float Switch (Oil Level Sensor) | 1 | 600 | 600 |
| 20×4 I2C LCD | 1 | 900 | 900 |
| Relay Module | 1 | 350 | 350 |
| Buzzer | 1 | 100 | 100 |
| Breadboard | 1 | 500 | 500 |
| Jumper Wires | 1 Pack | 300 | 300 |
| PCB and Soldering | - | 1,000 | 1,000 |
| Power Supply | 1 | 700 | 700 |
| Internet/Data | - | 500 | 500 |
| Printing and Binding | - | 2,000 | 2,000 |
| Miscellaneous | - | 1,000 | 1,000 |

Total Estimated Cost: KSh 11,000

Expected Outcomes

At the end of this project, the system should:

- Monitor transformer temperature, voltage, current, vibration, and oil level in real time.

- Display all measured values on an LCD.

- Upload transformer data to an IoT platform.

- Generate audible and visual alarms when abnormal conditions occur.

- Improve transformer reliability through early fault detection.

- Reduce maintenance costs and unexpected equipment failures.

CHAPTER FIVE

References

- Chapman, S. J. (2012). Electric Machinery Fundamentals (5th ed.). McGraw-Hill.

- Hughes, E. (2016). Electrical and Electronic Technology (12th ed.). Pearson Education.

- Kothari, C. R. (2019). Research Methodology: Methods and Techniques (4th ed.). New Age International.

- Rao, S. (2018). Power System Engineering. Khanna Publishers.

- Rajkamal. (2019). Internet of Things: Architecture and Design Principles. McGraw-Hill.

- Espressif Systems. (2024). ESP32 Technical Reference Manual.

- IEC 60076. (Latest edition). Power Transformers. International Electrotechnical Commission.

APPENDICES

Appendix A: System Block Diagram

Appendix C : Bill of Materials (BOM)

| Item | Quantity | Unit Cost (KSh) | Total (KSh) |
| --- | --- | --- | --- |
| ESP32 Development Board | 1 | 1,500 | 1,500 |
| ACS712 Current Sensor | 1 | 450 | 450 |
| ZMPT101B Voltage Sensor | 1 | 500 | 500 |
| DS18B20 Temperature Sensor | 1 | 350 | 350 |
| SW-420 Vibration Sensor | 1 | 250 | 250 |
| Float Switch (Oil Level Sensor) | 1 | 600 | 600 |
| 20×4 I2C LCD | 1 | 900 | 900 |
| Relay Module | 1 | 350 | 350 |
| Buzzer | 1 | 100 | 100 |
| Breadboard | 1 | 500 | 500 |
| Jumper Wires | 1 Pack | 300 | 300 |
| PCB and Soldering | - | 1,000 | 1,000 |
| Power Supply | 1 | 700 | 700 |
| Internet/Data | - | 500 | 500 |
| Printing and Binding | - | 2,000 | 2,000 |
| Miscellaneous | - | 1,000 | 1,000 |